## COVER
CONSORTIUM OF
SINOPEC PETROLEUM ENGINEERING CORPORATION.
AND
ZICOM EQUIPMENT PTE. LTD.
BANGLADESH GAS FIELDS COMPANY LIMITED.
[6 empty] | 29 Tuas Avenue 3 Singapore 639420 |  |  |  | Tel | : +65 6865 1765
[6 empty] | E-mail | : zepl@zicomgroup.com |  |  | Fax | : +65 6865 1764
ELECTRICAL CALCULATION SHEET
[8 empty] | Doc. No: | 252-07-CCS-001
|  | Job No. |  | : | 252
|  | Client |  | : | BANGLADESH GAS FIELDS COMPANY LIMITED
|  | Location |  | : | TITAS GAS FIELD, BRAHMANBARIA,BANGLADESH
|  | Item No. |  | : | -
|  | Description |  | : | ELECTRICAL LOAD CALCULATION
|  | Project Title. |  | : | 2 x 75 MMSCFD GLYCOL DEHYDRATION TYPE GAS PROCESS PLANT
|  | Year Built |  | : | 2014
A | 2015.10.28 |  | 2 | ISSUED FOR BIDDING | [5 empty] | AS | MH | VG
Rev. | Date |  | Page | Description of Revision | [5 empty] | Prepared | Checked | Approved
ZICOM

## Generator Sizing
GENERATOR SIZING
USER |  |  | BANGLADESH GAS FIELDS COMPANY LIMITED |  |  |  | DOC NO. | 240-07-CCS-001 |  | REV : A
LOCATION |  |  | TITAS GAS FIELD, BRAHMANBARIA, BANGLADESH |  |  |  | SERVICE | LOAD CALCULATION
PROJECT |  |  | 2 x 75 MMSCFD GLYCOL DEHYDRATION TYPE GAS PROCESS PLANT |  |  |  | TAG NO. | N/A
JOB NO. |  |  | 252 | LOCATION J |  |  | QUANTITY | N/A
S/L | EQUIPMENT |  | EQUIPMENT |  | VOLTAGE RATING | DESCRIPTION | QTY | CONNECTED LOAD | OPERATING LOAD | REMARKS
TAG No.
PLANT STARTER RACK :
1 | P-300A-J |  | CONDENSATE TRANSFER PUMP |  | 400 |  | 1 | 5500 | 5500
2 | P-300B-J |  |  |  | 400 |  | 1 | 5500
3 | P-200A-J |  | CONDENSATE RECYCLE PUMP |  | 400 |  | 1 | 1500 | 1500
4 | P-200B-J |  |  |  | 400 VAC |  | 1 | 1500
5 | AC-100A-J |  | INLET AIR COOLER |  | 400 VAC |  | 1 | 15000 | 15000
6 | AC-100B-J |  |  |  | 400 VAC |  | 1 | 15000
7 | E-300-J |  | OVERHEAD GAS COOLER |  | 400 VAC |  | 1 | 3000 | 3000
8 | P-400-J |  | KOD PUMP |  | 400 VAC |  | 1 | 1100 | 1100
9 | P-700-J |  | DEEP WELL PUMP |  | 400 |  | 1 | 7500 | 7500
10 | P-800-J |  | DEEP WELL PUMP |  | 400 |  | 1 | 7500 | 7500
11 | P-500A-J |  | ELECTRIC FIRE WATER PUMP |  | 400 |  | 1 | 134000 | 134000
12 | P-500B-J |  | CONTROL PANEL DIESEL FIRE PUMP |  | 230 |  | 1 | 500 | 500
13 | P-600-J |  | JOCKEY PUMP CONTROL PANEL |  | 400 |  | 1 | 11000 | 11000
14 | LCP-0701-J |  | FLARE & BURN PIT CONTROL PANEL |  | 230 |  | 1 | 3000 | 500
15 | LDP-1401-J |  | LIGHTING DISTRIBUTION PANEL |  | 400 |  | 1 | 15000 | 6000
16 | R-100-J |  | GLYCOL REBOILER |  | 400 |  | 1 | 5000 | 5000
17 | H-100-J |  | WATER BATH HEATER |  | 400 |  | 1 | 6000 | 200
18 | UPS-1-J |  | UPS SYSTEM-1 |  | 230 |  | 1 | 4800 | 2500
19 | UPS-2-J |  | UPS SYSTEM-2 |  | 230 |  | 1 | 4800
20 | UPS-3-J |  | UPS FOR FIRE & GAS SYSTEM |  | 230 |  | 1 | 800 | 100
21 | UPS-4-J |  | UPS FOR EMERGENCY LIGHTING |  | 230 |  | 1 | 1600 | 1200
22 | UPOB-J |  | UTILITY POWER OPERATION BUILDING |  | 400 |  | 1 | 22000 | 18000
23 | UPWB-J |  | UTILITY POWER WORKSHOP BUILDING |  | 400 |  | 1 | 10000 | 8000
24 | UPGB-J |  | UTILITY POWER GENERATOR BUILDING |  | 400 |  | 1 | 15000 | 12000
[8 empty] | Total: | 240100
240.1
|  | Total Load in Kw= |  |  | 240.1
|  | Base load =70% of Load= |  |  | 168.07
|  | Considering 100kW Plus Power Required= |  |  | 268.07
|  | Next Available Selected Generator Size= |  |  | 276
A | 2015.10.28 |  |  | ISSUED FOR APPROVAL |  |  |  | AS | MH | VG
REV | DATE |  |  | DESCRIPTION OF REVISION |  |  |  | PREPARED | CHECKED | APPROVED
ZICOM
CONSORTIUM OF
SINOPEC PETROLEUM ENGINEERING CORPORATION
AND
ZICOM EQUIPMENT PTE. LTD.
BANGLADESH GAS FIELDS COMPANY LIMITED