## COVER
CONSORTIUM OF
SINOPEC PETROLEUM ENGINEERING CORPORATION.
AND
ZICOM EQUIPMENT PTE. LTD.
BANGLADESH GAS FIELDS COMPANY LIMITED.
[6 empty] | 29 Tuas Avenue 3 Singapore 639420 |  |  |  | Tel | : +65 6865 1765
[6 empty] | E-mail | : zepl@zicomgroup.com |  |  | Fax | : +65 6865 1764
ELECTRICAL CALCULATION SHEET
[8 empty] | Doc. No: | 252-0214-EMEL-CS00-0008
|  | Job No. |  | : | 252
|  | Client |  | : | BANGLADESH GAS FIELDS COMPANY LIMITED
|  | Location |  | : | LOCATION J
|  | Item No. |  | : | -
|  | Description |  | : | FAULT LEVEL CALCULATION
|  | Project Title. |  | : | 2 x 75 MMSCFD GLYCOL DEHYDRATION TYPE GAS PROCESS PLANT
|  | Year Built |  | : | 2015
A | 28/10/2015 |  | 3 | ISSUED FOR APPROVAL | [5 empty] | AS | MH | VG
Rev. | Date |  | Page | Description of Revision | [5 empty] | Prepared | Checked | Approved
ZICOM

## AFC(Busbar Group B,C&D)
CONSORTIUM OF
| Electrical Calculation |  | ZICOM EQUIPMENT PTE LTD.
| Sheet |  | AND
SINOPEC PETROLEUM ENGINEERING CORPORATION
USER | BANGLADESH GAS FIELDS COMPANY LIMITED |  |  |  | DOC NO | 252-0214-EMEL-CS00-0008
LOCATION | TITAS GAS FIELD, BRAHMANBARIA, BANGLADESH |  |  |  | SERVICE | FAULT LEVEL CALCULATION
PROJECT | 2 x 75 MMSCFD GLYCOL DEHYDRATION TYPE GAS PROCESS PLANT |  |  |  | TAG NO
JOB NO | 252 | LOCATION J |  |  | QUANTITY
Generator KVA Rating | 345 | kVA
Line to Line Voltage | 400 | V
Line to Neutral Voltage | 230 | V
Full Load Ampere | 497.98 | A
Genset Alternator Percentage Impedance | 12.5 | %
Fault at zero distance/terminal |  |  | Fault at zero distance/terminal
Full Load Ampreres | 498 | A | Full Load Ampreres |  | 498 | A
Multiplier,M1 | 8 |  | Multiplier,M1 |  | 8
Fault at Generator terminal | 3984 | A | Fault at Generator terminal |  | 5976 | A
L-L Fault | 3.98 | kA | L-N Fault |  | 5.98 | kA
L-L-L Fault(AFC) | 4.58 | kA
For BUSBAR B, C& D
Fault at some distance from terminal |  |  | Fault at some distance from terminal
Distance from terminal, L | 230 | ft | Distance from terminal, L |  | 230 | ft
No. of Conductor,N | 1 |  | No. of Conductor,N |  | 1
Conductor factor,C | 799 |  | Conductor factor,C |  | 799
Factor,f | 4.9658 |  | Factor,f |  | 14.9587
Multiplier,M2 | 0.1676 |  | Multiplier,M2 |  | 0.0627
Fault after 1st distance | 668 | A | Fault after 1st distance |  | 374.7 | A
L-L Fault | 0.67 | kA | L-N Fault |  | 0.37 | kA
L-L-L Fault(AFC) | 0.77 | kA
Note |  | Formula
Reff. Drawing: 252-0214-EMEL-DW00-0008-J POWER |  | For L-L Fault |  | For L-N Fault
DISTRIBUTION SYSTEM FOR LOCATION J
For conductor factor, C reff. document is attached |  | FLA L-L= |  | FLA L-N =
FLA=Full Load Ampere
AFC=Available Fault Current |  | Multipier, M1 = |  | Multipier, M2 =
L-L Fault=Approx. 87% L-L-L Fault
Sub-transient Reactance Per Unit,Xd''=0.125 |  | Factor, f = |  | Factor, f =
For low resistance Percent Impedance≈12.5%
Percent Reactance data is found from Generator |  | I(SCA)= Short Circuit Current at the beginning of the circuit
datasheet of Model No: PG345B3 |  | L=Length of Cable
N=No. of Conductor Per Phase
C=Conductor factor(One over the impedance per foot)
E(L-L)=Phase to Phase Voltage or L-L Voltage
E(L-N)=Phase to Neutral Voltage or L-N Voltage
ZICOM
BANGLADESH GAS FIELDS COMPANY LIMITED

## AFC(Busbar Group E)
CONSORTIUM OF
| Electrical Calculation |  | ZICOM EQUIPMENT PTE LTD.
| Sheet |  | AND
SINOPEC PETROLEUM ENGINEERING CORPORATION
USER | BANGLADESH GAS FIELDS COMPANY LIMITED |  |  |  | DOC NO | 252-0214-EMEL-CS00-0008
LOCATION | TITAS GAS FIELD, BRAHMANBARIA, BANGLADESH |  |  |  | SERVICE | FAULT LEVEL CALCULATION
PROJECT | 2 x 75 MMSCFD GLYCOL DEHYDRATION TYPE GAS PROCESS PLANT |  |  |  | TAG NO
JOB NO | 252 | LOCATION J |  |  | QUANTITY
Generator KVA Rating | 345 | kVA
Line to Line Voltage | 400 | V
Line to Neutral Voltage | 230 | V
Full Load Ampere | 497.98 | A
Genset Alternator Percentage Impedance | 12.5 | %
Fault at zero distance/terminal |  |  | Fault at zero distance/terminal
Full Load Ampreres | 498 | A | Full Load Ampreres |  | 498 | A
Multiplier,M1 | 8 |  | Multiplier,M1 |  | 8
Fault at Generator terminal | 3984 | A | Fault at Generator terminal |  | 5976 | A
L-L Fault | 3.98 | kA | L-N Fault |  | 5.98 | kA
L-L-L Fault(AFC) | 4.58 | kA
For BUSBAR E
Fault at some distance from terminal |  |  | Fault at some distance from terminal
Distance from terminal, L | 65 | ft | Distance from terminal, L |  | 65 | ft
No. of Conductor,N | 1 |  | No. of Conductor,N |  | 1
Conductor factor,C | 981 |  | Conductor factor,C |  | 981
Factor,f | 1.143 |  | Factor,f |  | 3.4432
Multiplier,M2 | 0.4666 |  | Multiplier,M2 |  | 0.2251
Fault after 1st distance | 1859 | A | Fault after 1st distance |  | 1345.2 | A
L-L Fault | 1.86 | kA | L-N Fault |  | 1.35 | kA
L-L-L Fault(AFC) | 2.14 | kA
Note |  | Formula
Reff. Drawing: 252-0214-EMEL-DW00-0008-J POWER |  | For L-L Fault |  | For L-N Fault
DISTRIBUTION SYSTEM FOR LOCATION J
For conductor factor, C reff. document is attached |  | FLA L-L= |  | FLA L-N =
FLA=Full Load Ampere
AFC=Available Fault Current |  | Multipier, M1 = |  | Multipier, M2 =
L-L Fault=Approx. 87% L-L-L Fault
Sub-transient Reactance Per Unit,Xd''=0.125 |  | Factor, f = |  | Factor, f =
For low resistance Percent Impedance≈12.5%
Percent Reactance data is found from Generator |  | I(SCA)= Short Circuit Current at the beginning of the circuit
datasheet of Model No: PG345B3 |  | L=Length of Cable
N=No. of Conductor Per Phase
C=Conductor factor(One over the impedance per foot)
E(L-L)=Phase to Phase Voltage or L-L Voltage
E(L-N)=Phase to Neutral Voltage or L-N Voltage
ZICOM
BANGLADESH GAS FIELDS COMPANY LIMITED