## COVER
CONSORTIUM OF
SINOPEC PETROLEUM ENGINEERING CORPORATION.
AND
ZICOM EQUIPMENT PTE. LTD.
[6 empty] | 29 Tuas Avenue 3 Singapore 639420 |  |  |  | Tel | : +65 6865 1765
[6 empty] | E-mail | : zepl@zicomgroup.com |  |  | Fax | : +65 6865 1764
ELECTRICAL DATA SHEET
[8 empty] | Doc. No: | 252-0401-EMEL-DS00-0007
|  | Job No. |  | : | 252-I
|  | Client |  | : | BANGLADESH GAS FIELDS COMPANY LIMITED
|  | Location |  | : | TITAS GAS FIELD, BANGLADESH
|  | Item No. |  | : | -
|  | Description |  | : | LIGHTING SYSTEM
|  | Project Title. |  | : | 2×75MMSCFD TEG DEHYDRATION TYPE NATURAL GAS PROCESS PLANT
|  | Year Built |  | : | 2015
A | 2015-05-12 |  | 7 | ISSUED FOR APPROVAL | [5 empty] | AS | MH | VG
Rev. | Date |  | Page | Description of Revision | [5 empty] | Prepared | Checked | Approved
ZICOM

## High Mast Light (Circular)
ELECTRICAL DATASHEET
USER | BANGLADESH GAS FIELDS COMPANY LIMITED |  | DOC NO. | 252-0401-EMEL-DS00-0007 | REV : A
LOCATION | TITAS GAS FIELD, BANGLADESH |  | SERVICE | Plant Lighting
PROJECT | 2×75MMSCFD TEG DEHYDRATION TYPE NATURAL GAS PROCESS PLANT |  | TAG NO. | 02-L-0101, 02-L-0103, 02-L-0105
JOB NO. | 252 | Location I | QUANTITY | 3 Sets
GENERAL | 1 | Name | High Mast Light(Circular)
| 2 | Tag No. | 02-L-0101, 02-L-0103, 02-L-0105
| 3 | Quantity | 3 sets. (3 light per tower)
| 4 | Service | Plant Lighting
| 5 | Installation Location | Outdoor
| 6 | Cable | PVC Insulation
| 7 | Type of Lamp | Sodium Vapor Lamp
RATED | 8 | Input Voltage | 230 VAC
| 9 | Frequency | 50 Hz
| 10 | Phase | Single Phase
| 11 | Power | 3 numbers 200 Watt Explosion proof sodium light assembly at top
STRUCTURE | 12 | Mast Operation | Pneumatic Fixed
| 13 | Mounting Type | Pole
| 14 | Light Pole Height | 15 meter
| 15 | Light Pole Shape | Circle taper rod Polygon taper rod VTA
| 16 | Angle Between Lamps (Deg) | 30 60 90 120
| 17 | Refractor | Yes
| 18 | Degree of Explotion-Proof | Exd IIB T4
| 19 | Degree of Protection | IP65
OTHERS | 20 | Dimension | VTA
| 21 | Weight | VTA
| 22 | Manufacturer | Reputed
| 23 | Junction box | Explosion Proof, 4way
| 24 | Anchoring Bolt | Yes
| 25 | Gland | VTA
ZICOM
CONSORTIUM OF
SINOPEC PETROLEUM ENGINEERING CORPORATION
AND
ZICOM EQUIPMENT PTE. LTD.

## High Mast Light (Sectoral)
ELECTRICAL DATASHEET
USER | BANGLADESH GAS FIELDS COMPANY LIMITED |  | DOC NO. | 252-0401-EMEL-DS00-0007 | REV : A
LOCATION | TITAS GAS FIELD, BANGLADESH |  | SERVICE | Plant Lighting
PROJECT | 2×75MMSCFD TEG DEHYDRATION TYPE NATURAL GAS PROCESS PLANT |  | TAG NO. | 02-L-0102, 02-L-0104, 02-L-0106
JOB NO. | 252 | Location I | QUANTITY | 3 Sets
GENERAL | 1 | Name | High Mast Light(Sectoral)
| 2 | Tag No. | 02-L-0102, 02-L-0104, 02-L-0106
| 3 | Quantity | 3 sets. (3 light per tower)
| 4 | Service | Plant Lighting
| 5 | Installation Location | Outdoor
| 6 | Cable | PVC Insulation
| 7 | Type of Lamp | Sodium Vapor Lamp
RATED | 8 | Input Voltage | 230 VAC
| 9 | Frequency | 50 Hz
| 10 | Phase | Single Phase
| 11 | Power | 3 numbers 200 Watt Explosion proof sodium light assembly at top
STRUCTURE | 12 | Mast Operation | Pneumatic Fixed
| 13 | Mounting Type | Pole
| 14 | Light Pole Height | 15 meter
| 15 | Light Pole Shape | Circle taper rod Polygon taper rod VTA
| 16 | Angle Between Lamps (Deg) | 30 60 90 120
| 17 | Refractor | Yes
| 18 | Degree of Explotion-Proof | Exd IIB T4
| 19 | Degree of Protection | IP65
OTHERS | 20 | Dimension | VTA
| 21 | Weight | VTA
| 22 | Manufacturer | Reputed
| 23 | Junction box | Explosion Proof, 4way
| 24 | Anchoring Bolt | Yes
| 25 | Gland | VTA
ZICOM
CONSORTIUM OF
SINOPEC PETROLEUM ENGINEERING CORPORATION
AND
ZICOM EQUIPMENT PTE. LTD.

## Pipe Rack Light
ELECTRICAL DATASHEET
USER | BANGLADESH GAS FIELDS COMPANY LIMITED |  | DOC NO. | 252-0401-EMEL-DS00-0007 | REV : A
LOCATION | TITAS GAS FIELD, BANGLADESH |  | SERVICE | Pipe Rack Lighting
PROJECT | 2×75MMSCFD TEG DEHYDRATION TYPE NATURAL GAS PROCESS PLANT |  | TAG NO. | Mentioned Below
JOB NO. | 252 | Location I | QUANTITY | 16 Nos.
GENERAL | 1 | Name | PIpe Rack Light
| 2 | Tag No. | 02-L-0107, 02-L-0111, 02-L-0112, 02-L-0110, 02-L-0111, 02-L-0112,
02-L-0113, 02-L-0114, 02-L-0115, 02-L-0116, 02-L-0117, 02-L-0118,
02-L-0119, 02-L-0120, 02-L-0121, 02-L-0144
| 3 | Quantity | 16 Nos.
| 4 | Service | Pipe Rack Lighting
| 5 | Installation Location (Zone) | Zone 2
| 6 | Cable | PVC Insulation
| 7 | Type of Lamp | Sodium Vapor Lamp
RATED | 8 | Input Voltage | 230 VAC
| 9 | Frequency | 50 Hz
| 10 | Phase | Single Phase
| 11 | Power | 100W
STRUCTURE | 12 | Housing | VTA
| 13 | Mounting Type | Pole
| 15 | Lamp Pole | Single Arm Double Arm
| 16 | Refractor | Yes
| 17 | Degree of Explotion-Proof | Exd IIB T4
| 18 | Degree of Protection | IP65
OTHERS | 19 | Dimension | VTA
| 20 | Weight | VTA
| 21 | Manufacturer | Reputed
| 22 | Junction box | Explosion Proof, 4way
| 23 | Gland | VTA
ZICOM
CONSORTIUM OF
SINOPEC PETROLEUM ENGINEERING CORPORATION
AND
ZICOM EQUIPMENT PTE. LTD.

## Exit Light
ELECTRICAL DATASHEET
USER | BANGLADESH GAS FIELDS COMPANY LIMITED |  | DOC NO. | 252-0401-EMEL-DS00-0007 | REV : A
LOCATION | TITAS GAS FIELD, BANGLADESH |  | SERVICE | Exit Light
PROJECT | 2×75MMSCFD TEG DEHYDRATION TYPE NATURAL GAS PROCESS PLANT |  | TAG NO. | N/A
JOB NO. | 252 | Location I | QUANTITY | 18 Nos.
GENERAL | 1 | Name | Exit Light
| 2 | Tag No. | N/A
| 3 | Quantity | 18 Nos.
| 4 | Service | Exit Door
| 5 | Installation Location (Zone) | Indoor
| 6 | Cable | PVC Insulation
| 7 | Type of Lamp | VTA
RATED | 8 | Input Voltage | 230 VAC
| 9 | Frequency | 50 Hz
| 10 | Phase | Single Phase
| 11 | Power | VTA
| 11 | Back up Battery | Yes
STRUCTURE | 12 | Housing | VTA
| 13 | Mounting Type | Wall mounted
| 16 | Refractor | Yes
OTHERS | 17 | Dimension | VTA
| 18 | Weight | VTA
| 19 | Manufacturer | Reputed
| 20 | Gland | VTA
Exit Light
ZICOM
CONSORTIUM OF
SINOPEC PETROLEUM ENGINEERING CORPORATION
AND
ZICOM EQUIPMENT PTE. LTD.

## Shed Light
ELECTRICAL DATASHEET
USER | BANGLADESH GAS FIELDS COMPANY LIMITED |  | DOC NO. | 252-0401-EMEL-DS00-0007 | REV : A
LOCATION | TITAS GAS FIELD, BANGLADESH |  | SERVICE | Shed Light
PROJECT | 2×75MMSCFD TEG DEHYDRATION TYPE NATURAL GAS PROCESS PLANT |  | TAG NO. | Mentioned Below
JOB NO. | 252 | Location I | QUANTITY | 10 Nos.
GENERAL | 1 | Name | Shed Light
| 2 | Tag | 02-L-122, 02-L-123, 02-L-124 + 7 Nos. Spare
| 3 | Quantity | 10 Nos.
| 4 | Service | Shed Lighting
| 5 | Installation Location (Zone) | Zone 2
| 6 | Cable | PVC Insulation
| 7 | Type of Lamp | Fluorescent Tube
| 8 | No. of Lamp each shed | 2 (Two)
RATED | 9 | Input Voltage | 230 VAC
| 10 | Frequency | 50 Hz
| 11 | Phase | Single Phase
| 12 | Lamp Power | 2 x 18 Watt
STRUCTURE | 13 | Housing | VTA
| 14 | Mounting Type | Wall Mounted
| 15 | Refractor | Yes
| 16 | Degree of Explotion-Proof | Exd IIB T4
| 17 | Degree of Protection | IP65
OTHERS | 18 | Dimension | VTA
| 19 | Weight | VTA
| 20 | Manufacturer | Reputed
| 21 | Junction box | Explosion Proof, 2way
| 22 | Gland | VTA
Shed Light
ZICOM
CONSORTIUM OF
SINOPEC PETROLEUM ENGINEERING CORPORATION
AND
ZICOM EQUIPMENT PTE. LTD.

## Loading Arm Shed Light
ELECTRICAL DATASHEET
USER | BANGLADESH GAS FIELDS COMPANY LIMITED |  | DOC NO. | 240-0301-EMEL-DS00-0005 | REV : A
LOCATION | TITAS GAS FIELD, BANGLADESH |  | SERVICE | Shed Light for Loading Arm
PROJECT | 2×75MMSCFD TEG DEHYDRATION TYPE NATURAL GAS PROCESS PLANT |  | TAG NO. | Mentioned Below
JOB NO. | 252 | Location I | QUANTITY | 2 Nos.
GENERAL | 1 | Name | Shed Light (Loading Arm)
02-L-0125, 02-L-0126
| 3 | Quantity | 2 Nos.
| 4 | Service | Shed Light for Loading Arm
| 5 | Installation Location (Zone) | Zone 2
| 6 | Cable | PVC Insulation
| 7 | Type of Lamp | Sodium Vapor Lamp
RATED | 8 | Input Voltage | 230 VAC
| 9 | Frequency | 50 Hz
| 10 | Phase | Single Phase
| 11 | Power | 200W
STRUCTURE | 12 | Housing | VTA
| 13 | Mounting Type | Bracket Mounted
| 16 | Refractor | Yes
| 17 | Degree of Explotion-Proof | Exd IIB T4
| 18 | Degree of Protection | IP65
OTHERS | 19 | Dimension | VTA
| 20 | Weight | VTA
| 21 | Manufacturer | Reputed
| 22 | Junction box | Explosion Proof, 2way
| 23 | Gland | VTA
Shed Light for Loading Arm
ZICOM
CONSORTIUM OF
SINOPEC PETROLEUM ENGINEERING CORPORATION
AND
ZICOM EQUIPMENT PTE. LTD.